## on grid menjual
On grid menjual ke grid |  |  |  |  | Asumsi PLTS setiap tahunnya energi yang dihasilkan PLTS menurun 0,5%
Tahun | Investasi Awal (Rp) | Arus Kas Keluar (Rp) | Self-consumption kWh | Energi yang di ekspor (kWh) | Arus Kas Masuk (Rp) | Arus Kas Bersih(Rp) | Kumulatif arus kas bersih | Faktor Diskonto | Present Value NCF (Rp) |  | IRR | IRR
- | -9891493200 | 9891493200 |  |  |  | -9891493200 | -9891493200 | 1 | 9891493200 | -9891493200 | 12% | 13%
1 |  | 98914932 | 903027.31 | 234910.26 | 1507168810.54 | 1408253878.54 | -8483239321.46 | 0.90909 | 1280230798.6727 | -8611262401.3273 | 1257369534.4107 | 1246242370.3894
2 |  | 98914932 | 898512.1735 | 233735.7087 | 1499632966.4873 | 1400718034.4873 | -7082521286.9727 | 0.82645 | 1157618210.3201 | -7453644191.0072 | 1116643841.2686 | 1096967683.0506
3 |  | 98914932 | 894019.6126 | 232567.0302 | 1492134801.6549 | 1393219869.6549 | -5689301417.3178 | 0.75131 | 1046746708.9819 | -6406897482.0253 | 991666384.0815 | 965571256.7528
4 |  | 98914932 | 889549.5145 | 231404.195 | 1484674127.6466 | 1385759195.6466 | -4303542221.6712 | 0.68301 | 946492176.5225 | -5460405305.5028 | 880675021.1491 | 849912066.744
5 |  | 98914932 | 885101.7669 | 230247.174 | 1477250757.0084 | 1378335825.0084 | -2925206396.6629 | 0.62092 | 855838104.084 | -4604567201.4188 | 782104763.3088 | 748105464.1673
6 |  | 98914932 | 880676.2581 | 229095.9382 | 1469864503.2233 | 1370949571.2233 | -1554256825.4396 | 0.56447 | 773865292.374 | -3830701909.0448 | 694565718.3464 | 658492479.2351
7 |  | 98914932 | 876272.8768 | 227950.4585 | 1462515180.7072 | 1363600248.7072 | -190656576.7324 | 0.51316 | 699742537.6455 | -3130959371.3993 | 616823502.5359 | 579612799.5279
8 |  | 98914932 | 871891.5124 | 226810.7062 | 1455202604.8037 | 1356287672.8037 | 1165631096.0713 | 0.46651 | 632718209.0504 | -2498241162.3489 | 547781843.3606 | 510180983.4574
9 |  | 98914932 | 867532.0549 | 225676.6526 | 1447926591.7796 | 1349011659.7796 | 2514642755.8509 | 0.4241 | 572112632.0693 | -1926128530.2797 | 486467128.3336 | 449065521.5968
10 |  | 402144729.1363 | 863194.3946 | 224548.2694 | 1440686958.8207 | 1038542229.6844 | 3553184985.5353 | 0.38554 | 400402987.444 | -1525725542.8357 | 334382803.0276 | 305942439.902
11 |  | 98914932 | 858878.4226 | 223425.528 | 1433483524.0266 | 1334568592.0266 | 4887753577.562 | 0.35049 | 467758149.9448 | -1057967392.8909 | 383656579.4885 | 347918899.9877
12 |  | 98914932 | 854584.0305 | 222308.4004 | 1426316106.4065 | 1327401174.4065 | 6215154751.9685 | 0.31863 | 422950921.6308 | -635016471.26 | 340710819.8166 | 306239266.4023
13 |  | 98914932 | 850311.1104 | 221196.8584 | 1419184525.8745 | 1320269593.8745 | 7535424345.843 | 0.28966 | 382435072.9949 | -252581398.2652 | 302571714.9292 | 269552184.7648
14 |  | 98914932 | 846059.5548 | 220090.8741 | 1412088603.2451 | 1313173671.2451 | 8848598017.0881 | 0.26333 | 345799669.9707 | 93218271.7055 | 268701350.5423 | 237259689.6032
15 |  | 98914932 | 841829.257 | 218990.4197 | 1405028160.2289 | 1306113228.2289 | 10154711245.317 | 0.23939 | 312673122.4139 | 405891394.1194 | 238622003.5851 | 208835427.5323
16 |  | 98914932 | 837620.1108 | 217895.4676 | 1398003019.4277 | 1299088087.4277 | 11453799332.7447 | 0.21763 | 282719417.7822 | 688610811.9016 | 211909407.7017 | 183816081.8406
17 |  | 98914932 | 833432.0102 | 216805.9903 | 1391013004.3306 | 1292098072.3306 | 12745897405.0753 | 0.19784 | 255634715.3067 | 944245527.2083 | 188186772.1632 | 161793823.8724
18 |  | 98914932 | 829264.8501 | 215721.9603 | 1384057939.3089 | 1285143007.3089 | 14031040412.3842 | 0.17986 | 231144266.1549 | 1175389793.3632 | 167119469.9125 | 142409668.2711
19 |  | 98914932 | 825118.5259 | 214643.3505 | 1377137649.6124 | 1278222717.6124 | 15309263129.9966 | 0.16351 | 208999628.3857 | 1384389421.7489 | 148410319.89 | 125347623.8655
20 |  | 215823145.441 | 820992.9333 | 213570.1338 | 1370251961.3643 | 1154428815.9233 | 16463691945.92 | 0.14864 | 171598487.4945 | 1555987909.2433 | 119675900.8627 | 100183981.8887
21 |  | 98914932 | 816887.9686 | 212502.2831 | 1363400701.5575 | 1264485769.5575 | 17728177715.4775 | 0.13513 | 170870683.9745 | 1726858593.2178 | 117040311.8041 | 97110599.0173
22 |  | 98914932 | 812803.5288 | 211439.7717 | 1356583698.0497 | 1257668766.0497 | 18985846481.5272 | 0.12285 | 154499543.9986 | 1881358137.2164 | 103936904.113 | 85475277.3757
23 |  | 98914932 | 808739.5111 | 210382.5728 | 1349800779.5595 | 1250885847.5595 | 20236732329.0867 | 0.11168 | 139696627.0663 | 2021054764.2827 | 92300309.5544 | 75233883.2562
24 |  | 98914932 | 804695.8136 | 209330.66 | 1343051775.6617 | 1244136843.6617 | 21480869172.7484 | 0.10153 | 126311737.0401 | 2147366501.3228 | 81966352.1014 | 66219440.6216
25 |  | 98914932 | 800672.3345 | 208284.0067 | 1336336516.7834 | 1237421584.7834 | 22718290757.5317 | 0.092296 | 114209060.3334 | 2261575561.6562 | 72789229.2161 | 58284973.0797
|  | 12784504510.5773 |  |  | 35502795268.1091 | 22718290757.5317 |  |  | 12153068761.6562 |  | 10546077985.5037 | 9875773886.2022
[9 empty] | 2261575561.6562 |  | 654584785.5037 | -15719313.7978
[9 empty] | IRR = |  | 12.98%
[9 empty] | NPV = |  | 2261575561.6562
[9 empty] | PBP = |  | 7.1406
[9 empty] | PI = |  | 1.2286
No | item | seri | harga | jumlah | harga total | sumber
1 | Inverter | SG110CX | 78650000 | 10 | 786500000 | https://www.tokopedia.com/tridayaadhinata/sungrow-110cx-wifi-dongle?extParam=whid%3D8625683
2 | PV Module | JA SOLAR 540 Wp | 2350000 | 3420 | 8037000000 | https://www.tokopedia.com/surya-solusi/solar-panel-ja-solar-550-wp-mono-sni?extParam=ivf%3Dfalse%26src%3Dsearch&refined=true
3 | DC Cable | Cable 6mm2 ,100m | 3100000 | 36 | 111600000 | https://www.tokopedia.com/badank/100m-black-red-6mm2-solar-pv-cable-h1z2z2-k-1500v-tinned-copper?extParam=ivf%3Dfalse%26src%3Dsearch&refined=true
4 | Mounting grounding clip | EZ-GZ-AE | 4000 | 2080 | 8320000 | https://tokopedia.link/vMUDWMBpjyb
5 | Mounting grounding Lug | EZ-GL-U | 15000 | 2080 | 31200000 | https://tokopedia.link/cE6pk9Fpjyb
6 | Mounting End Clamp | ER-EC-AE/35/L50 | 13000 | 2080 | 27040000 | https://tokopedia.link/wCcbJRLpjyb
7 | Mounting Mid Clamp | ER-EC-AE/30-40/L50 478 | 22000 | 4160 | 91520000 | https://tokopedia.link/81HiUS4pjyb
8 | Grounding cable | 1x6mm Per Meter Super Kabel | 75800 | 3600 | 272880000 | https://www.tokopedia.com/visiotekindo/kabel-nyy-35-mm-kabel-grounding-35mm?extParam=ivf%3Dfalse%26src%3Dsearch
9 | Lighting protecrion | Current cr120 | 2500000 | 3 | 7500000 | https://www.tokopedia.com/indoledlighting/current-cr120-penangkal-petir-lighting-protection-radius-120m-120-m
10 | Kabel Tray | Galvanis powder coating Hotdip 3m | 141191 | 1200 | 169429200 | https://www.tokopedia.com/rajaboxpanel/kabel-cable-tray-tipe-u-elektro-galvanis-powder-coating-hotdip-2mm?extParam=ivf%3Dfalse&src=topads
11 | MC4 connector | Male-Female | 5200 | 3420 | 17784000 | https://www.tokopedia.com/panelsuryaku-8/mc4-socket-connector-solar-panel-surya-solarcell-konektor-ip67
12 | Mounting Rail | Rail 2200mm | 78000 | 3120 | 243360000 | https://www.tokopedia.com/activ-shop/mounting-bracket-solar-pv-solar-module-panel-surya-rail-2200mm-lokal-1-1-mtr-8432b?extParam=ivf%3Dfalse%26src%3Dsearch
13 | Mounting Rail Clamp | ER-RC-AE | 14000 | 6240 | 87360000 | https://tokopedia.link/5LdE1W0qjyb
| total |  | 86968191 |  | 9891493200

## hybrid menjual
LCOE (Rp)
Hybrid menjual ke grid |  |  |  |  | Asumsi PLTS setiap tahunnya energi yang dihasilkan PLTS menurun 0,5%
Tahun | Investasi Awal (Rp) | Arus Kas Keluar (Rp) pertahun | Self-consumption(kWh) | Energi yang di ekspor (kWh) | Arus Kas Masuk (Rp) | Arus Kas Bersih(Rp) | kumulative arus kas bersih(Rp) | Faktor Diskonto | Present Value (Rp) | IRR | IRR
- | 12884194420 | 12884194420 |  |  |  | -12884194420 | -12884194420 | 1 | -12884194420 | 10% | 11%
1 |  | 128841944.2 | 1116162.99 | 87396.79 | 1710847317.42 | 1582005373.22 | -11302189046.78 | 0.90909 | 1438186702.9273 | 1438186702.9273 | 1425230065.964
2 |  | 128841944.2 | 1105029.2642 | 86916.1077 | 1705698049.7596 | 1576856105.5596 | -9725332941.2204 | 0.82645 | 1303186864.0988 | 1303186864.0988 | 1279811789.27
3 |  | 128841944.2 | 1099504.1179 | 86438.0691 | 1685704716.4983 | 1556862772.2983 | -8168470168.9221 | 0.75131 | 1169694043.8004 | 1169694043.8004 | 1138364640.9728
4 |  | 128841944.2 | 1094006.5973 | 85962.6597 | 1688574253.6088 | 1559732309.4088 | -6608737859.5133 | 0.68301 | 1065318154.0939 | 1065318154.0939 | 1027443983.5823
5 |  | 128841944.2 | 1088536.5643 | 85489.8651 | 1668792305.79 | 1539950361.59 | -5068787497.9233 | 0.62092 | 956188015.9639 | 956188015.9639 | 913885587.2298
6 |  | 128841944.2 | 1083093.8815 | 85019.6708 | 1671622468.0527 | 1542780523.8527 | -3526006974.0705 | 0.56447 | 870859385.5096 | 870859385.5096 | 824833469.1741
7 |  | 128841944.2 | 1077678.412 | 84552.0626 | 1652049665.9967 | 1523207721.7967 | -2002799252.2739 | 0.51316 | 781646408.1917 | 781646408.1917 | 733665810.7372
8 |  | 128841944.2 | 1072290.02 | 84087.0263 | 1654840964.1139 | 1525999019.9139 | -476800232.36 | 0.46651 | 711889804.9827 | 711889804.9827 | 662171408.0655
9 |  | 128841944.2 | 1066928.5699 | 83624.5476 | 1635475091.9201 | 1506633147.7201 | 1029832915.3601 | 0.4241 | 638959529.7091 | 638959529.7091 | 588980218.9159
10 |  | 462706347.9799 | 1061593.927 | 83164.6126 | 1638228030.2061 | 1175521682.2261 | 2205354597.5862 | 0.38554 | 453214496.1612 | 453214496.1612 | 414000490.9429
11 |  | 128841944.2 | 1056285.9574 | 82707.2072 | 1619066895.4999 | 1490224951.2999 | 3695579548.8861 | 0.35049 | 522314754.2856 | 522314754.2856 | 472823511.4687
12 |  | 128841944.2 | 1051004.5276 | 82252.3176 | 1621781971.9588 | 1492940027.7588 | 5188519576.6449 | 0.31863 | 475696701.8373 | 475696701.8373 | 426743207.1405
13 |  | 128841944.2 | 1045749.505 | 81799.9299 | 1602823405.6416 | 1473981461.4416 | 6662501038.0866 | 0.28966 | 426959925.7719 | 426959925.7719 | 379571238.6755
14 |  | 128841944.2 | 1040520.7575 | 81350.0302 | 1605501112.0445 | 1476659167.8445 | 8139160205.931 | 0.26333 | 388850510.8511 | 388850510.8511 | 342577284.9066
15 |  | 128841944.2 | 1035318.1537 | 80902.6051 | 1586742968.0458 | 1457901023.8458 | 9597061229.7768 | 0.23939 | 349009913.8758 | 349009913.8758 | 304707650.9697
16 |  | 709389426.8338 | 1030141.5629 | 80457.6407 | 1589383790.0065 | 879994363.1727 | 10477055592.9495 | 0.21763 | 191512412.7575 | 191512412.7575 | 165696078.3161
17 |  | 128841944.2 | 1024990.8551 | 80015.1237 | 1570823945.039 | 1441982000.839 | 11919037593.7886 | 0.19784 | 285288451.516 | 285288451.516 | 244607179.5852
18 |  | 128841944.2 | 1019865.9008 | 79575.0405 | 1573428362.0897 | 1444586417.8897 | 13363624011.6783 | 0.17986 | 259821565.0409 | 259821565.0409 | 220764841.1384
19 |  | 128841944.2 | 1014766.5713 | 79137.3778 | 1555064715.407 | 1426222771.207 | 14789846782.8853 | 0.16351 | 233198819.7911 | 233198819.7911 | 196358980.7893
20 |  | 257561124.6567 | 1009692.7384 | 78702.1222 | 1557633201.0721 | 1300072076.4153 | 16089918859.3006 | 0.14864 | 193247430.1313 | 193247430.1313 | 161253019.1359
21 |  | 128841944.2 | 1004644.2748 | 78269.2606 | 1539463674.2288 | 1410621730.0288 | 17500540589.3294 | 0.13513 | 190618119.7465 | 190618119.7465 | 157626058.1991
22 |  | 128841944.2 | 999621.0534 | 77838.7796 | 1541996696.0983 | 1413154751.8983 | 18913695341.2277 | 0.12285 | 173600371.3072 | 173600371.3072 | 142260453.8595
23 |  | 128841944.2 | 994622.9481 | 77410.6663 | 1524019232.7129 | 1395177288.5129 | 20308872629.7406 | 0.11168 | 155810829.3775 | 155810829.3775 | 126532149.5177
24 |  | 128841944.2 | 989649.8334 | 76984.9077 | 1526517252.5151 | 1397675308.3151 | 21706547938.0557 | 0.10153 | 141899821.4792 | 141899821.4792 | 114197028.1425
25 |  | 128841944.2 | 984701.5842 | 76599.9831 | 1508773468.478 | 1379931524.278 | 23086479462.3337 | 0.092296 | 127362157.4492 | 127362157.4492 | 101574119.5367
|  | 17148374091.8705 | 26166400.5675 | 2046654.4038 | 40234853554.2042 | 23086479462.3337 |  |  | 13504335190.6565 | 13504335190.6565 | 12565680266.2358
[10 empty] | 620140770.6565 | -318514153.7642
No | item | seri | harga | jumlah | harga total | sumber |  |  | IRR= | 10.66%
1 | PV Module | JA SOLAR 540 Wp | 2350000 | 3420 | 8037000000 | https://tokopedia.link/umaeRLJojyb |  |  | NPV= | 620140770.6565
2 | Baterai | EVE LF100MA 48 V 100ah Lifepo4 | 7800000 | 342 | 2667600000 | https://www.tokopedia.com/baterailab/baterai-lithium-lifepo4-3-2v-100ah-discharge-capacity-test-prove-eve-100ah-c7528 |  |  | PBP | 8.3165
3 | DC Cable | Cable 6mm2 , 100m | 3100000 | 36 | 111600000 | https://www.tokopedia.com/badank/100m-black-red-6mm2-solar-pv-cable-h1z2z2-k-1500v-tinned-copper?extParam=ivf%3Dfalse%26src%3Dsearch&refined=true |  |  | PI | 1.0481
4 | Mounting grounding clip | EZ-GZ-AE | 4000 | 2080 | 8320000 | https://tokopedia.link/vMUDWMBpjyb
5 | Mounting grounding Lug | EZ-GL-U | 15000 | 2080 | 31200000 | https://tokopedia.link/cE6pk9Fpjyb
6 | Mounting End Clamp | ER-EC-AE/35/L50 | 13000 | 2080 | 27040000 | https://tokopedia.link/wCcbJRLpjyb
7 | Mounting Mid Clamp | ER-EC-AE/30-40/L50 478 | 22000 | 4160 | 91520000 | https://tokopedia.link/81HiUS4pjyb
8 | Hybrid Inverter | ATESS HPS 100 | 86595828 | 10 | 865958280 | https://indonesian.alibaba.com/p-detail/ATESS-1600700727460.html?spm=a2700.galleryofferlist.p_offer.d_title.375435e4XxCGbF&s=p
9 | beamasuk hybrid inverter |  | 238642940 |  | 238642940
10 | Lighting protecrion | Current cr120 | 2500000 | 3 | 7500000 | https://www.tokopedia.com/indoledlighting/current-cr120-penangkal-petir-lighting-protection-radius-120m-120-m
11 | Grounding cable | 1x6mm Per Meter Super Kabel | 75800 | 3600 | 272880000 | https://www.tokopedia.com/visiotekindo/kabel-nyy-35-mm-kabel-grounding-35mm?extParam=ivf%3Dfalse%26src%3Dsearch
12 | MC4 connector | Male-Female | 5200 | 3420 | 17784000 | https://www.tokopedia.com/panelsuryaku-8/mc4-socket-connector-solar-panel-surya-solarcell-konektor-ip67
13 | Kabel Tray | Galvanis powder coating Hotdip 3m | 141191 | 1200 | 169429200 | https://www.tokopedia.com/rajaboxpanel/kabel-cable-tray-tipe-u-elektro-galvanis-powder-coating-hotdip-2mm?extParam=ivf%3Dfalse&src=topads
14 | Mounting Rail | Rail 2200mm | 78000 | 3120 | 243360000
15 | Mounting Rail Clamp | ER-RC-AE | 14000 | 6240 | 87360000 | https://tokopedia.link/5LdE1W0qjyb
16 | kWh Exim | Edmi Mk6N | 7000000 | 1 | 7000000 | http://en.integra-solusi.co.id/product/kwh-meter-edmi-mk6n-class-05s-p969115.aspx
| Total |  | 348356959 |  | 12884194420

## ongrid
On-grid tidak menjual |  |  |  | Asumsi PLTS setiap tahunnya energi yang dihasilkan PLTS menurun 0,5%
Tahun | Investasi Awal (Rp) | Arus Kas Keluar (Rp) | self-consumption (kWh) | Arus Kas Masuk (Rp) | Arus Kas Bersih(Rp) | Kumulatif arus kas bersih | Faktor Diskonto | Present Value NCF (Rp) | IRR | IRR
- | -9891493200 | 9891493200 |  |  | -9891493200 | -9891493200 | 1 | 9891493200 | 10% | 11%
1 |  | 98914932 | 903027.31 | 1303971435.64 | 1205056503.64 | -8686436696.36 | 0.90909 | 1095505912.4 | 1095505912.4 | 1085636489.7658
2 |  | 98914932 | 894019.6126 | 1290964320.5695 | 1192049388.5695 | -7494387307.7905 | 0.82645 | 985164783.9417 | 985164783.9417 | 967494025.2979
3 |  | 98914932 | 889549.5145 | 1284509498.9666 | 1185594566.9666 | -6308792740.8239 | 0.75131 | 890754746.0305 | 890754746.0305 | 866896529.0832
4 |  | 98914932 | 885101.7669 | 1278086951.4718 | 1179172019.4718 | -5129620721.3521 | 0.68301 | 805390355.4892 | 805390355.4892 | 776757133.0712
5 |  | 98914932 | 880676.2581 | 1271696516.7145 | 1172781584.7145 | -3956839136.6376 | 0.62092 | 728205093.2403 | 728205093.2403 | 695988788.9714
6 |  | 98914932 | 876272.8768 | 1265338034.1309 | 1166423102.1309 | -2790416034.5067 | 0.56447 | 658415432.5653 | 658415432.5653 | 623617422.5565
7 |  | 98914932 | 871891.5124 | 1259011343.9602 | 1160096411.9602 | -1630319622.5465 | 0.51316 | 595312891.7277 | 595312891.7277 | 558770194.2649
8 |  | 98914932 | 867532.0549 | 1252716287.2404 | 1153801355.2404 | -476518267.3061 | 0.46651 | 538256847.5156 | 538256847.5156 | 500664979.5034
9 |  | 98914932 | 863194.3946 | 1246452705.8042 | 1147537773.8042 | 671019506.4981 | 0.4241 | 486668036.8628 | 486668036.8628 | 448600941.9428
10 |  | 402144729.1363 | 858878.4226 | 1240220442.2752 | 838075713.1389 | 1509095219.637 | 0.38554 | 323114467.2346 | 323114467.2346 | 295157258.2054
11 |  | 98914932 | 854584.0305 | 1234019340.0638 | 1135104408.0638 | 2644199627.7008 | 0.35049 | 397847170.3008 | 397847170.3008 | 360149688.5663
12 |  | 98914932 | 850311.1104 | 1227849243.3635 | 1128934311.3635 | 3773133939.0643 | 0.31863 | 359713262.771 | 359713262.771 | 322695513.3659
13 |  | 98914932 | 846059.5548 | 1221709997.1467 | 1122795065.1467 | 4895929004.211 | 0.28966 | 325233736.1171 | 325233736.1171 | 289135735.2891
14 |  | 98914932 | 841829.257 | 1215601447.161 | 1116686515.161 | 6012615519.372 | 0.26333 | 294058460.704 | 294058460.704 | 259065492.421
15 |  | 98914932 | 837620.1108 | 1209523439.9251 | 1110608507.9251 | 7123224027.2971 | 0.23939 | 265870846.759 | 265870846.759 | 232122005.5832
16 |  | 98914932 | 833432.0102 | 1203475822.7255 | 1104560890.7255 | 8227784918.0227 | 0.21763 | 240384632.0762 | 240384632.0762 | 207980204.7762
17 |  | 98914932 | 829264.8501 | 1197458443.6119 | 1098543511.6119 | 9326328429.6346 | 0.19784 | 217340977.3272 | 217340977.3272 | 186348810.0896
18 |  | 98914932 | 825118.5259 | 1191471151.3938 | 1092556219.3938 | 10418884649.0284 | 0.17986 | 196505839.528 | 196505839.528 | 166966819.8609
19 |  | 98914932 | 820992.9333 | 1185513795.6369 | 1086598863.6369 | 11505483512.6653 | 0.16351 | 177667597.0277 | 177667597.0277 | 149600363.7706
20 |  | 215823145.441 | 816887.9686 | 1179586226.6587 | 963763081.2177 | 12469246593.883 | 0.14864 | 143257240.9479 | 143257240.9479 | 119539300.4722
21 |  | 98914932 | 812803.5288 | 1173688295.5254 | 1074773363.5254 | 13544019957.4084 | 0.13513 | 145234738.2347 | 145234738.2347 | 120097603.1657
22 |  | 98914932 | 808739.5111 | 1167819854.0478 | 1068904922.0478 | 14612924879.4561 | 0.12285 | 131310665.8066 | 131310665.8066 | 107605270.5048
23 |  | 98914932 | 804695.8136 | 1161980754.7775 | 1063065822.7775 | 15675990702.2336 | 0.11168 | 118721232.7018 | 118721232.7018 | 96412122.4896
24 |  | 98914932 | 800672.3345 | 1156170851.0036 | 1057255919.0036 | 16733246621.2373 | 0.10153 | 107338539.4104 | 107338539.4104 | 86383069.9577
25 |  | 98914932 | 796668.9728 | 1150389996.7486 | 1051475064.7486 | 17784721685.9859 | 0.092296 | 97046940.6593 | 97046940.6593 | 77397067.9252
|  | 12784504510.5773 |  | 30569226196.5632 | 17784721685.9859 |  |  | 10324320447.3797 | 10324320447.3797 | 9601082830.9003
[8 empty] | 432827247.3797 | 432827247.3797 | -290410369.0997
[9 empty] | IRR = | 10.6%
[9 empty] | NPV = | 432827247.3797
[9 empty] | PBP = | 8.4153
[9 empty] | PI = | 1.0438
No | item | seri | harga | jumlah | harga total | sumber
1 | Inverter | SG110CX | 78650000 | 10 | 786500000 | https://tokopedia.link/2dXuW31njyb
2 | PV Module | JA SOLAR 540 Wp | 2350000 | 3420 | 8037000000 | https://tokopedia.link/umaeRLJojyb
3 | DC Cable | Cable 6mm2 , 100 m | 3100000 | 36 | 111600000 | https://tokopedia.link/Gb0xmrUojyb
4 | Mounting grounding clip | EZ-GZ-AE | 4000 | 2080 | 8320000 | https://tokopedia.link/vMUDWMBpjyb
5 | Mounting grounding Lug | EZ-GL-U | 15000 | 2080 | 31200000 | https://tokopedia.link/cE6pk9Fpjyb
6 | Mounting End Clamp | ER-EC-AE/35/L50 | 13000 | 2080 | 27040000 | https://tokopedia.link/wCcbJRLpjyb
7 | Mounting Mid Clamp | ER-EC-AE/30-40/L50 478 | 22000 | 4160 | 91520000 | https://tokopedia.link/81HiUS4pjyb
8 | Lighting protecrion | Current cr120 | 2500000 | 3 | 7500000 | https://www.tokopedia.com/indoledlighting/current-cr120-penangkal-petir-lighting-protection-radius-120m-120-m
9 | Grounding cable | 1x6mm Per Meter Super Kabel | 75800 | 3600 | 272880000 | https://www.tokopedia.com/visiotekindo/kabel-nyy-35-mm-kabel-grounding-35mm?extParam=ivf%3Dfalse%26src%3Dsearch
10 | Kabel Tray | Galvanis powder coating Hotdip 2mm | 141191 | 1200 | 169429200 | https://www.tokopedia.com/rajaboxpanel/kabel-cable-tray-tipe-u-elektro-galvanis-powder-coating-hotdip-2mm?extParam=ivf%3Dfalse&src=topads
11 | MC4 connector | Male-Female | 5200 | 3420 | 17784000 | https://www.tokopedia.com/panelsuryaku-8/mc4-socket-connector-solar-panel-surya-solarcell-konektor-ip67
12 | Mounting Rail | Rail 2200mm | 78000 | 3120 | 243360000
13 | Mounting Rail Clamp | ER-RC-AE | 14000 | 6240 | 87360000 | https://tokopedia.link/5LdE1W0qjyb
| total |  | 86968191 |  | 9891493200

## hybrid
Hybrid tidak menjual ke grid | [6 empty] | Asumsi PLTS setiap tahunnya energi yang dihasilkan PLTS menurun 0,5%
Tahun | Investasi Awal (Rp) | Arus Kas Keluar (Rp) pertahun | Present Value Pembangkitan Energi Listrik (kWh) | Penghematan atau Energi yang di import(kWh) | Arus Kas Masuk (Rp) | Arus Kas Bersih(Rp) | kumulative arus kas bersih(Rp) | Faktor Diskonto | Present Value (Rp) | IRR | IRR
- | 12884194420 | 12884194420 | 1238207 |  |  | -12884194420 | -12884194420 | 1 | -12884194420 | 9% | 10%
1 |  | 128841944.2 | 1232015.965 | 1116162.99 | 1611739357.56 | 1482897413.36 | -11401297006.64 | 0.90909 | 1348088557.6 | 1360456342.5321 | 1348088557.6
2 |  | 128841944.2 | 1225855.8852 | 1105029.2642 | 1595662257.4683 | 1466820313.2683 | -9934476693.3717 | 0.82645 | 1212248192.7838 | 1234593311.3949 | 1212248192.7838
3 |  | 128841944.2 | 1219726.6057 | 1099504.1179 | 1587683946.181 | 1458842001.981 | -8475634691.3907 | 0.75131 | 1096049588.2652 | 1126493693.9489 | 1096049588.2652
4 |  | 128841944.2 | 1213627.9727 | 1094006.5973 | 1579745526.4501 | 1450903582.2501 | -7024731109.1406 | 0.68301 | 990986669.1142 | 1027856676.4908 | 990986669.1142
5 |  | 128841944.2 | 1207559.8329 | 1088536.5643 | 1571846798.8178 | 1443004854.6178 | -5581726254.5227 | 0.62092 | 895992483.5101 | 937854145.597 | 895992483.5101
6 |  | 128841944.2 | 1201522.0337 | 1083093.8815 | 1563987564.8238 | 1435145620.6238 | -4146580633.899 | 0.56447 | 810102288.673 | 855730442.8917 | 810102288.673
7 |  | 128841944.2 | 1195514.4235 | 1077678.412 | 1556167626.9996 | 1427325682.7996 | -2719254951.0993 | 0.51316 | 732443761.4878 | 780796027.0358 | 732443761.4878
8 |  | 128841944.2 | 1189536.8514 | 1072290.02 | 1548386788.8646 | 1419544844.6646 | -1299710106.4347 | 0.46651 | 662228146.5747 | 712421690.0205 | 662228146.5747
9 |  | 128841944.2 | 1183589.1671 | 1066928.5699 | 1540644854.9203 | 1411802910.7203 | 112092804.2856 | 0.4241 | 598742252.0478 | 650033279.2976 | 598742252.0478
10 |  | 462706347.9799 | 1177671.2213 | 1061593.927 | 1532941630.6457 | 1070235282.6658 | 1182328086.9514 | 0.38554 | 412622031.3425 | 452078949.3191 | 412622031.3425
11 |  | 128841944.2 | 1171782.8652 | 1056285.9574 | 1525276922.4925 | 1396434978.2925 | 2578763065.2439 | 0.35049 | 489441940.9139 | 541164427.4843 | 489441940.9139
12 |  | 128841944.2 | 1165923.9509 | 1051004.5276 | 1517650537.88 | 1388808593.68 | 3967571658.9239 | 0.31863 | 442517217.8474 | 493769681.5757 | 442517217.8474
13 |  | 128841944.2 | 1160094.3311 | 1045749.505 | 1510062285.1906 | 1381220340.9906 | 5348791999.9145 | 0.28966 | 400090333.3527 | 450524581.8731 | 400090333.3527
14 |  | 128841944.2 | 1154293.8595 | 1040520.7575 | 1502511973.7647 | 1373670029.5647 | 6722462029.4792 | 0.26333 | 361730251.8879 | 411065900.4667 | 361730251.8879
15 |  | 128841944.2 | 1148522.3902 | 1035318.1537 | 1494999413.8958 | 1366157469.6958 | 8088619499.175 | 0.23939 | 327047236.4315 | 375062195.8556 | 327047236.4315
16 |  | 709389426.8338 | 1142779.7782 | 1030141.5629 | 1487524416.8264 | 778134989.9926 | 8866754489.1676 | 0.21763 | 169344845.4002 | 195988675.2567 | 169344845.4002
17 |  | 128841944.2 | 1137065.8793 | 1024990.8551 | 1480086794.7422 | 1351244850.5422 | 10217999339.7098 | 0.19784 | 267336590.0585 | 312236440.2006 | 267336590.0585
18 |  | 128841944.2 | 1131380.5499 | 1019865.9008 | 1472686360.7685 | 1343844416.5685 | 11561843756.2783 | 0.17986 | 241702230.5903 | 284886604.0485 | 241702230.5903
19 |  | 128841944.2 | 1125723.6472 | 1014766.5713 | 1465322928.9647 | 1336480984.7647 | 12898324741.043 | 0.16351 | 218525320.5968 | 259931745.5046 | 218525320.5968
20 |  | 257561124.6567 | 1120095.0289 | 1009692.7384 | 1457996314.3199 | 1200435189.6631 | 14098759930.7061 | 0.14864 | 178437041.7994 | 214194719.0175 | 178437041.7994
21 |  | 128841944.2 | 1114494.5538 | 1004644.2748 | 1450706332.7483 | 1321864388.5483 | 15420624319.2544 | 0.13513 | 178624289.5179 | 216386641.3029 | 178624289.5179
22 |  | 128841944.2 | 1108922.081 | 999621.0534 | 1443452801.0845 | 1314610856.8845 | 16735235176.1389 | 0.12285 | 161494650.5845 | 197430506.6167 | 161494650.5845
23 |  | 128841944.2 | 1103377.4706 | 994622.9481 | 1436235537.0791 | 1307393592.8791 | 18042628769.018 | 0.11168 | 146007307.9647 | 180134500.5193 | 146007307.9647
24 |  | 128841944.2 | 1097860.5833 | 989649.8334 | 1429054359.3937 | 1300212415.1937 | 19342841184.2117 | 0.10153 | 132004842.9728 | 164353273.3109 | 132004842.9728
25 |  | 128841944.2 | 1092371.2804 | 984701.5842 | 1421909087.5967 | 1293067143.3967 | 20635908327.6084 | 0.092296 | 119344922.7098 | 149954197.8465 | 119344922.7098
|  | 17148374091.8705 | 29021308.2082 | 26166400.5675 | 37784282419.4789 | 20635908327.6084 |  |  | 12593152994.0274 | 13585398649.4081 | 12593152994.0274
[10 empty] | 701204229.4081 | -291041425.9726
No | item | seri | harga | jumlah | harga total | sumber |  |  | IRR= | 9.707%
1 | PV Module | JA SOLAR 540 Wp | 2350000 | 3420 | 8037000000 | https://tokopedia.link/umaeRLJojyb |  |  | NPV= | -291041425.9726
2 | Baterai | EVE LF100MA 48 V 100ah Lifepo4 | 7800000 | 342 | 2667600000 | https://www.tokopedia.com/baterailab/baterai-lithium-lifepo4-3-2v-100ah-discharge-capacity-test-prove-eve-100ah-c7528 |  |  | PBP | 9.9206
3 | DC Cable | Cable 6mm2 , 100 m | 3100000 | 36 | 111600000 | https://www.tokopedia.com/badank/100m-black-red-6mm2-solar-pv-cable-h1z2z2-k-1500v-tinned-copper?extParam=ivf%3Dfalse%26src%3Dsearch&refined=true |  |  | PI | 0.97741
4 | Mounting grounding clip | EZ-GZ-AE | 4000 | 2080 | 8320000 | https://tokopedia.link/vMUDWMBpjyb
5 | Mounting grounding Lug | EZ-GL-U | 15000 | 2080 | 31200000 | https://tokopedia.link/cE6pk9Fpjyb
6 | Mounting End Clamp | ER-EC-AE/35/L50 | 13000 | 2080 | 27040000 | https://tokopedia.link/wCcbJRLpjyb
7 | Mounting Mid Clamp | ER-EC-AE/30-40/L50 478 | 22000 | 4160 | 91520000 | https://tokopedia.link/81HiUS4pjyb
8 | Hybrid Inverter | ATESS HPS 100 | 86595828 | 10 | 865958280 | https://indonesian.alibaba.com/p-detail/ATESS-1600700727460.html?spm=a2700.galleryofferlist.p_offer.d_title.375435e4XxCGbF&s=p
9 | beacukai |  | 238642940 |  | 238642940
10 | Lighting protecrion | Current cr120 | 2500000 | 3 | 7500000 | https://www.tokopedia.com/indoledlighting/current-cr120-penangkal-petir-lighting-protection-radius-120m-120-m
11 | Grounding cable | 1x6mm Per Meter Super Kabel | 75800 | 3600 | 272880000 | https://www.tokopedia.com/visiotekindo/kabel-nyy-35-mm-kabel-grounding-35mm?extParam=ivf%3Dfalse%26src%3Dsearch
12 | MC4 connector | Male-Female | 5200 | 3420 | 17784000 | https://www.tokopedia.com/panelsuryaku-8/mc4-socket-connector-solar-panel-surya-solarcell-konektor-ip67
13 | Kabel Tray | Galvanis powder coating Hotdip 2mm | 141191 | 1200 | 169429200 | https://www.tokopedia.com/rajaboxpanel/kabel-cable-tray-tipe-u-elektro-galvanis-powder-coating-hotdip-2mm?extParam=ivf%3Dfalse&src=topads
14 | Mounting Rail | Rail 2200mm | 78000 | 3120 | 243360000
15 | Mounting Rail Clamp | ER-RC-AE | 14000 | 6240 | 87360000 | https://tokopedia.link/5LdE1W0qjyb
16 | kWh Exim | Edmi Mk6N | 7000000 | 1 | 7000000 | http://en.integra-solusi.co.id/product/kwh-meter-edmi-mk6n-class-05s-p969115.aspx
| Total |  | 348356959 |  | 12884194420

## aktual on grid menjual
On grid menjual ke grid |  |  |  |  | Asumsi PLTS setiap tahunnya energi yang dihasilkan PLTS menurun 0,5%
Tahun | Investasi Awal (Rp) | Arus Kas Keluar (Rp) | Self-consumption(kWh) | Energi yang di ekspor (kWh) | Arus Kas Masuk (Rp) | Arus Kas Bersih(Rp) | Kumulatif arus kas bersih | Faktor Diskonto | Present Value NCF (Rp) | IRR | IRR
- | -9891493200 | 9891493200 |  |  |  | -9891493200 | -9891493200 | 1 | 9891493200 | 14% | 15%
1 |  | 98914932 | 1093996 | 22721 | 1599383889 | 1500468957 | -8391024243 | 0.90909 | 1364062688.1818 | 1316200839.4737 | 1304755614.7826
2 |  | 98914932 | 1088526.02 | 22607.395 | 1591386969.555 | 1492472037.555 | -6898552205.445 | 0.82645 | 1233447964.9215 | 1148408770.0485 | 1128523279.8147
3 |  | 98914932 | 1083083.3899 | 22494.358 | 1583430034.7072 | 1484515102.7072 | -5414037102.7378 | 0.75131 | 1115338168.8259 | 1002005409.6991 | 976092777.3204
4 |  | 98914932 | 1077667.973 | 22381.8862 | 1575512884.5337 | 1476597952.5337 | -3937439150.2041 | 0.68301 | 1008536269.745 | 874264525.3004 | 844249671.7972
5 |  | 98914932 | 1072279.6331 | 22269.9768 | 1567635320.111 | 1468720388.111 | -2468718762.0931 | 0.62092 | 911959806.5899 | 762807346.2913 | 730213607.6271
6 |  | 98914932 | 1066918.2349 | 22158.6269 | 1559797143.5105 | 1460882211.5105 | -1007836550.5826 | 0.56447 | 824629923.277 | 665558283.3151 | 631579694.4123
7 |  | 98914932 | 1061583.6437 | 22047.8338 | 1551998157.7929 | 1453083225.7929 | 445246675.2103 | 0.51316 | 745661453.7805 | 580706289.7689 | 546267806.6665
8 |  | 98914932 | 1056275.7255 | 21937.5946 | 1544238167.0039 | 1445323235.0039 | 1890569910.2143 | 0.46651 | 674253955.9179 | 506671147.2168 | 472478729.3039
9 |  | 98914932 | 1050994.3469 | 21827.9066 | 1536516976.1689 | 1437602044.1689 | 3328171954.3832 | 0.4241 | 609683603.0995 | 442074047.2416 | 408656224.6293
10 |  | 402144729.1363 | 1045739.3752 | 21718.7671 | 1528834391.2881 | 1126689662.1518 | 4454861616.5349 | 0.38554 | 434387638.5122 | 303917561.6144 | 278500453.0295
11 |  | 98914932 | 1040510.6783 | 21610.1733 | 1521190219.3316 | 1422275287.3316 | 5877136903.8666 | 0.35049 | 498498811.5929 | 336535047.5346 | 305708433.8465
12 |  | 98914932 | 1035308.1249 | 21502.1224 | 1513584268.235 | 1414669336.235 | 7291806240.1016 | 0.31863 | 450757247.3943 | 293627497.6651 | 264411814.0921
13 |  | 98914932 | 1030131.5843 | 21394.6118 | 1506016346.8938 | 1407101414.8938 | 8698907654.9954 | 0.28966 | 407587158.5718 | 256190093.6002 | 228693317.8099
14 |  | 98914932 | 1024980.9264 | 21287.6387 | 1498486265.1593 | 1399571333.1593 | 10098478988.1547 | 0.26333 | 368550874.6517 | 223525523.0057 | 197799538.2713
15 |  | 98914932 | 1019856.0217 | 21181.2005 | 1490993833.8335 | 1392078901.8335 | 11490557889.9883 | 0.23939 | 333252621.1935 | 195025356.9096 | 171078820.006
16 |  | 98914932 | 1014756.7416 | 21075.2945 | 1483538864.6644 | 1384623932.6644 | 12875181822.6527 | 0.21763 | 301334509.8601 | 170158721.0132 | 147967517.7459
17 |  | 98914932 | 1009682.9579 | 20969.9181 | 1476121170.3411 | 1377206238.3411 | 14252388060.9937 | 0.19784 | 272472912.2318 | 148462410.7997 | 127978110.913
18 |  | 98914932 | 1004634.5431 | 20865.0685 | 1468740564.4893 | 1369825632.4893 | 15622213693.4831 | 0.17986 | 246375180.6462 | 129532266.4463 | 110688923.104
19 |  | 98914932 | 999611.3704 | 20760.7431 | 1461396861.6669 | 1362481929.6669 | 16984695623.15 | 0.16351 | 222776682.8573 | 113015646.9938 | 95735229.8472
20 |  | 215823145.441 | 994613.3135 | 20656.9394 | 1454089877.3586 | 1238266731.9176 | 18222962355.0675 | 0.14864 | 184060459.4938 | 90098420.6678 | 75658442.723
21 |  | 98914932 | 989640.247 | 20553.6547 | 1446819427.9718 | 1347904495.9718 | 19570866851.0393 | 0.13513 | 182143104.1012 | 86031450.2293 | 71615078.8601
22 |  | 98914932 | 984692.0457 | 20450.8864 | 1439585330.8319 | 1340670398.8319 | 20911537249.8712 | 0.12285 | 164695960.3859 | 75061163.3509 | 61939762.0688
23 |  | 98914932 | 979768.5855 | 20348.632 | 1432387404.1778 | 1333472472.1778 | 22245009722.049 | 0.11168 | 148919749.1622 | 65489620.5223 | 53571490.1025
24 |  | 98914932 | 974869.7426 | 20246.8889 | 1425225467.1569 | 1326310535.1569 | 23571320257.2059 | 0.10153 | 134654470.2086 | 57138493.7055 | 46333707.3037
25 |  | 98914932 | 969995.3939 | 20145.6544 | 1418099339.8211 | 1319184407.8211 | 24890504665.0269 | 0.092296 | 121755441.6995 | 49852188.2231 | 40073705.3532
|  | 12784504510.5773 |  |  | 37675009175.6043 | 24890504665.0269 |  |  | 12959796656.9019 | 9892358120.6368 | 9320571751.4308
[9 empty] | 3068303456.9019 | 864920.6368 | -570921448.5692
[9 empty] | IRR = | 14%
[9 empty] | NPV = | 3068303456.9019
[9 empty] | PBP = | 6.6936
[9 empty] | PI = | 1.3102
No | item | seri | harga | jumlah | harga total | sumber
1 | Inverter | SG110CX | 78650000 | 10 | 786500000 | https://www.tokopedia.com/tridayaadhinata/sungrow-110cx-wifi-dongle?extParam=whid%3D8625683
2 | PV Module | JA SOLAR 540 Wp | 2350000 | 3420 | 8037000000 | https://tokopedia.link/umaeRLJojyb
3 | DC Cable | Cable 6mm2 ,100m | 3100000 | 36 | 111600000 | https://www.tokopedia.com/badank/100m-black-red-6mm2-solar-pv-cable-h1z2z2-k-1500v-tinned-copper?extParam=ivf%3Dfalse%26src%3Dsearch&refined=true
4 | Mounting grounding clip | EZ-GZ-AE | 4000 | 2080 | 8320000 | https://tokopedia.link/vMUDWMBpjyb
5 | Mounting grounding Lug | EZ-GL-U | 15000 | 2080 | 31200000 | https://tokopedia.link/cE6pk9Fpjyb
6 | Mounting End Clamp | ER-EC-AE/35/L50 | 13000 | 2080 | 27040000 | https://tokopedia.link/wCcbJRLpjyb
7 | Mounting Mid Clamp | ER-EC-AE/30-40/L50 478 | 22000 | 4160 | 91520000 | https://tokopedia.link/81HiUS4pjyb
8 | Grounding cable | 1x6mm Per Meter Super Kabel | 75800 | 3600 | 272880000 | https://www.tokopedia.com/visiotekindo/kabel-nyy-35-mm-kabel-grounding-35mm?extParam=ivf%3Dfalse%26src%3Dsearch
9 | Lighting protecrion | Current cr120 | 2500000 | 3 | 7500000 | https://www.tokopedia.com/indoledlighting/current-cr120-penangkal-petir-lighting-protection-radius-120m-120-m
10 | Kabel Tray | Galvanis powder coating Hotdip 3m | 141191 | 1200 | 169429200 | https://www.tokopedia.com/rajaboxpanel/kabel-cable-tray-tipe-u-elektro-galvanis-powder-coating-hotdip-2mm?extParam=ivf%3Dfalse&src=topads
11 | MC4 connector | Male-Female | 5200 | 3420 | 17784000 | https://www.tokopedia.com/panelsuryaku-8/mc4-socket-connector-solar-panel-surya-solarcell-konektor-ip67
12 | Mounting Rail | Rail 2200mm | 78000 | 3120 | 243360000 | https://www.tokopedia.com/activ-shop/mounting-bracket-solar-pv-solar-module-panel-surya-rail-2200mm-lokal-1-1-mtr-8432b?extParam=ivf%3Dfalse%26src%3Dsearch
13 | Mounting Rail Clamp | ER-RC-AE | 14000 | 6240 | 87360000 | https://tokopedia.link/5LdE1W0qjyb
| total |  | 86968191 |  | 9891493200

## aktual hybrid menjual
LCOE (Rp)
Hybrid menjual ke grid |  |  |  | 1311.8721 | Asumsi PLTS setiap tahunnya energi yang dihasilkan PLTS menurun 0,5%
Tahun | Investasi Awal (Rp) | Arus Kas Keluar (Rp) pertahun | Penghematan atau Energi yang di import(kWh) | Energi yang di ekspor (kWh) | Arus Kas Masuk (Rp) | Arus Kas Bersih(Rp) | kumulative arus kas bersih(Rp) | Faktor Diskonto | Present Value (Rp) | IRR | IRR
- | 12884194420 | 12884194420 |  |  |  | -12884194420 | -12884194420 | 1 | -12884194420 | 11% | 12%
1 |  | 128841944.2 | 1226878 | 1455 | 1773261802 | 1644419857.8 | -11239774562.2 | 0.90909 | 1494927143.4545 | 1481459331.3514 | 1468232015.8929
2 |  | 128841944.2 | 1214639.892 | 1446.9975 | 1755580899.1408 | 1626738954.9408 | -9613035607.2592 | 0.82645 | 1344412359.4552 | 1320297828.8619 | 1296826335.2526
3 |  | 128841944.2 | 1208566.6925 | 1439.039 | 1746802174.1975 | 1617960229.9975 | -7995075377.2617 | 0.75131 | 1215597468.0673 | 1183038575.4619 | 1151632133.4599
4 |  | 128841944.2 | 1202523.859 | 1431.1243 | 1738067347.3914 | 1609225403.1914 | -6385849974.0703 | 0.68301 | 1099122603.095 | 1060046617.4632 | 1022691835.9564
5 |  | 128841944.2 | 1196511.2397 | 1423.2531 | 1729376199.207 | 1600534255.007 | -4785315719.0633 | 0.62092 | 993805847.2204 | 949839179.2371 | 908186119.7885
6 |  | 128841944.2 | 1190528.6835 | 1415.4252 | 1720728511.2264 | 1591886567.0264 | -3193429152.0369 | 0.56447 | 898578466.6892 | 851087565.1535 | 806499276.2397
7 |  | 128841944.2 | 1184576.0401 | 1407.6404 | 1712124066.1242 | 1583282121.9242 | -1610147030.1127 | 0.51316 | 812474074.3149 | 762601150.8378 | 716196425.5093
8 |  | 128841944.2 | 1178653.1599 | 1399.8984 | 1703562647.6615 | 1574720703.4615 | -35426326.6512 | 0.46651 | 734618829.9338 | 683313037.501 | 636003280.88
9 |  | 128841944.2 | 1172759.8941 | 1392.1989 | 1695044040.6808 | 1566202096.4808 | 1530775769.8295 | 0.4241 | 664222579.0075 | 612267196.5951 | 564788177.1381
10 |  | 462706347.9799 | 1166896.0946 | 1384.5418 | 1686568031.1006 | 1223861683.1207 | 2754637452.9502 | 0.38554 | 471851659.1171 | 431025088.9619 | 394050707.2537
11 |  | 128841944.2 | 1161061.6142 | 1376.9268 | 1678134405.9099 | 1549292461.7099 | 4303929914.6601 | 0.35049 | 543017556.3418 | 491564646.9338 | 445384561.002
12 |  | 128841944.2 | 1155256.3061 | 1369.3537 | 1669742953.1628 | 1540901008.9628 | 5844830923.6229 | 0.31863 | 490978548.4965 | 440452413.5091 | 395510909.6952
13 |  | 128841944.2 | 1149480.0246 | 1361.8223 | 1661393461.9734 | 1532551517.7734 | 7377382441.3963 | 0.28966 | 443925584.8104 | 394653863.1269 | 351221252.9179
14 |  | 128841944.2 | 1143732.6244 | 1354.3323 | 1653085722.5103 | 1524243778.3103 | 8901626219.7066 | 0.26333 | 401381026.0107 | 353616668.2739 | 311890476.2988
15 |  | 128841944.2 | 1138013.9613 | 1346.8835 | 1644819525.9913 | 1515977581.7913 | 10417603801.4979 | 0.23939 | 362912980.1027 | 316845904.0188 | 276963436.3536
16 |  | 709389426.8338 | 1132323.8915 | 1339.4756 | 1636594664.6785 | 927205237.8447 | 11344809039.3426 | 0.21763 | 201786874.6122 | 174585517.9698 | 151247259.2668
17 |  | 128841944.2 | 1126662.2721 | 1332.1085 | 1628410931.8724 | 1499568987.6724 | 12844378027.015 | 0.19784 | 296681729.859 | 254375810.8316 | 218403736.8905
18 |  | 128841944.2 | 1121028.9607 | 1324.7819 | 1620268121.9075 | 1491426177.7075 | 14335804204.7226 | 0.17986 | 268246107.5614 | 227922995.2004 | 193944448.8392
19 |  | 128841944.2 | 1115423.8159 | 1317.4956 | 1612166030.1467 | 1483324085.9467 | 15819128290.6693 | 0.16351 | 242535341.0378 | 204220554.8648 | 172223978.7031
20 |  | 257561124.6567 | 1109846.6968 | 1310.2494 | 1604104452.976 | 1346543328.3192 | 17165671618.9885 | 0.14864 | 200155085.6131 | 167017030.0769 | 139591790.8878
21 |  | 128841944.2 | 1104297.4633 | 1303.043 | 1596083187.7997 | 1467241243.5997 | 18632912862.5882 | 0.13513 | 198269146.9412 | 163952850.5286 | 135807279.7473
22 |  | 128841944.2 | 1098775.976 | 1295.8762 | 1588102033.0353 | 1459260088.8353 | 20092172951.4235 | 0.12285 | 179264226.3102 | 146901818.2601 | 120596917.1085
23 |  | 128841944.2 | 1093282.0961 | 1288.7489 | 1580160788.1083 | 1451318843.9083 | 21543491795.3318 | 0.11168 | 162080614.8598 | 131623768.8695 | 107089850.6177
24 |  | 128841944.2 | 1087815.6857 | 1281.6608 | 1572259253.4471 | 1443417309.2471 | 22986909104.5789 | 0.10153 | 146543805.4773 | 117934377.2511 | 95095368.3284
25 |  | 128841944.2 | 1082376.6072 | 1275.2525 | 1564397957.1799 | 1435556012.9799 | 24422465117.5588 | 0.092296 | 132496075.1571 | 105668531.7341 | 84444151.4244
|  | 17148374091.8705 | 28761911.5515 | 34073.1297 | 41570839209.4293 | 24422465117.5588 |  |  | 13999885733.5461 | 13026312322.8741 | 12164521725.4525
[10 empty] | 142117902.8741 | -719672694.5475
No | item | seri | harga | jumlah | harga total | sumber |  |  | IRR= | 11.16%
1 | PV Module | JA SOLAR 540 Wp | 2350000 | 3420 | 8037000000 | https://tokopedia.link/umaeRLJojyb |  |  | NPV= | 1115691313.5461
2 | Baterai | EVE LF100MA 48 V 100ah Lifepo4 | 7800000 | 342 | 2667600000 | https://www.tokopedia.com/baterailab/baterai-lithium-lifepo4-3-2v-100ah-discharge-capacity-test-prove-eve-100ah-c7528 |  |  | PBP | 8.0226
3 | DC Cable | Cable 6mm2 , 100m | 3100000 | 36 | 111600000 | https://www.tokopedia.com/badank/100m-black-red-6mm2-solar-pv-cable-h1z2z2-k-1500v-tinned-copper?extParam=ivf%3Dfalse%26src%3Dsearch&refined=true |  |  | PI | 1.0866
4 | Mounting grounding clip | EZ-GZ-AE | 4000 | 2080 | 8320000 | https://tokopedia.link/vMUDWMBpjyb
5 | Mounting grounding Lug | EZ-GL-U | 15000 | 2080 | 31200000 | https://tokopedia.link/cE6pk9Fpjyb
6 | Mounting End Clamp | ER-EC-AE/35/L50 | 13000 | 2080 | 27040000 | https://tokopedia.link/wCcbJRLpjyb
7 | Mounting Mid Clamp | ER-EC-AE/30-40/L50 478 | 22000 | 4160 | 91520000 | https://tokopedia.link/81HiUS4pjyb
8 | Hybrid Inverter | ATESS HPS 100 | 86595828 | 10 | 865958280 | https://indonesian.alibaba.com/p-detail/ATESS-1600700727460.html?spm=a2700.galleryofferlist.p_offer.d_title.375435e4XxCGbF&s=p
9 | beamasuk hybrid inverter |  | 238642940 |  | 238642940
10 | Lighting protecrion | Current cr120 | 2500000 | 3 | 7500000 | https://www.tokopedia.com/indoledlighting/current-cr120-penangkal-petir-lighting-protection-radius-120m-120-m
11 | Grounding cable | 1x6mm Per Meter Super Kabel | 75800 | 3600 | 272880000 | https://www.tokopedia.com/visiotekindo/kabel-nyy-35-mm-kabel-grounding-35mm?extParam=ivf%3Dfalse%26src%3Dsearch
12 | MC4 connector | Male-Female | 5200 | 3420 | 17784000 | https://www.tokopedia.com/panelsuryaku-8/mc4-socket-connector-solar-panel-surya-solarcell-konektor-ip67
13 | Kabel Tray | Galvanis powder coating Hotdip 3m | 141191 | 1200 | 169429200 | https://www.tokopedia.com/rajaboxpanel/kabel-cable-tray-tipe-u-elektro-galvanis-powder-coating-hotdip-2mm?extParam=ivf%3Dfalse&src=topads
14 | Mounting Rail | Rail 2200mm | 78000 | 3120 | 243360000
15 | Mounting Rail Clamp | ER-RC-AE | 14000 | 6240 | 87360000 | https://tokopedia.link/5LdE1W0qjyb
16 | kWh Exim | Edmi Mk6N | 7000000 | 1 | 7000000 | http://en.integra-solusi.co.id/product/kwh-meter-edmi-mk6n-class-05s-p969115.aspx
| Total |  | 348356959 |  | 12884194420

## aktual ongrid
On-grid tidak menjual |  |  |  | Asumsi PLTS setiap tahunnya energi yang dihasilkan PLTS menurun 0,5%
Tahun | Investasi Awal (Rp) | Arus Kas Keluar (Rp) | Penghematan atau Energi yang di import(kWh) | Arus Kas Masuk (Rp) | Arus Kas Bersih(Rp) | Kumulatif arus kas bersih | Faktor Diskonto | Present Value NCF (Rp) | IRR | IRR
- | -9891493200 | 9891493200 |  |  | -9891493200 | -9891493200 | 1 | 9891493200 | 13% | 14%
1 |  | 98914932 | 1093996.9 | 1579731523.6 | 1480816591.6 | -8410676608.4 | 0.90909 | 1346196901.4545 | 1310457160.708 | 1298961922.4561
2 |  | 98914932 | 1083084.2809 | 1563973701.6521 | 1465058769.6521 | -6945617838.7479 | 0.82645 | 1210792371.6133 | 1147355916.4007 | 1127315150.5479
3 |  | 98914932 | 1077668.8595 | 1556153833.1438 | 1457238901.1438 | -5488378937.6041 | 0.75131 | 1094845154.8789 | 1009939656.9151 | 983594750.5736
4 |  | 98914932 | 1072280.5152 | 1548373063.9781 | 1449458131.9781 | -4038920805.626 | 0.68301 | 989999407.1294 | 888979817.3293 | 858195572.8181
5 |  | 98914932 | 1066919.1126 | 1540631198.6582 | 1441716266.6582 | -2597204538.9678 | 0.62092 | 895192371.7693 | 782505828.6208 | 748782251.8001
6 |  | 98914932 | 1061584.5171 | 1532928042.6649 | 1434013110.6649 | -1163191428.3028 | 0.56447 | 809463016.3257 | 688783065.6344 | 653317082.4215
7 |  | 98914932 | 1056276.5945 | 1525263402.4516 | 1426348470.4516 | 263157042.1488 | 0.51316 | 731942297.0382 | 606284599.0565 | 570022083.7259
8 |  | 98914932 | 1050995.2115 | 1517637085.4393 | 1418722153.4393 | 1681879195.5881 | 0.46651 | 661844355.0465 | 533666329.06 | 497345897.2055
9 |  | 98914932 | 1045740.2355 | 1510048900.0121 | 1411133968.0121 | 3093013163.6003 | 0.4241 | 598458555.0385 | 469745095.8221 | 433934903.5914
10 |  | 402144729.1363 | 1040511.5343 | 1502498655.5121 | 1100353926.3758 | 4193367089.976 | 0.38554 | 424234072.3116 | 324151445.5251 | 296813659.9197
11 |  | 98914932 | 1035308.9766 | 1494986162.2345 | 1396071230.2345 | 5589438320.2106 | 0.35049 | 489314449.4387 | 363952493.4347 | 330334712.2835
12 |  | 98914932 | 1030132.4317 | 1487511231.4234 | 1388596299.4234 | 6978034619.6339 | 0.31863 | 442449574.3548 | 320357342.0481 | 288215801.5469
13 |  | 98914932 | 1024981.7696 | 1480073675.2662 | 1381158743.2662 | 8359193362.9002 | 0.28966 | 400072490.6861 | 281983587.6565 | 251466727.2514
14 |  | 98914932 | 1019856.8607 | 1472673306.8899 | 1373758374.8899 | 9732951737.7901 | 0.26333 | 361753515.9732 | 248205924.8927 | 219402935.71
15 |  | 98914932 | 1014757.5764 | 1465309940.3555 | 1366395008.3555 | 11099346746.1455 | 0.23939 | 327104101.298 | 218473926.7474 | 191427133.7875
16 |  | 98914932 | 1009683.7885 | 1457983390.6537 | 1359068458.6537 | 12458415204.7992 | 0.21763 | 295772894.1364 | 192303078.9371 | 167018166.6215
17 |  | 98914932 | 1004635.3696 | 1450693473.7004 | 1351778541.7004 | 13810193746.4996 | 0.19784 | 267442178.009 | 169266887.6874 | 145721312.8877
18 |  | 98914932 | 999612.1928 | 1443440006.3319 | 1344525074.3319 | 15154718820.8315 | 0.17986 | 241824652.8719 | 148989932.4268 | 127139816.9529
19 |  | 98914932 | 994614.1318 | 1436222806.3003 | 1337307874.3003 | 16492026695.1318 | 0.16351 | 218660523.6434 | 131141750.2681 | 110927500.2868
20 |  | 215823145.441 | 989641.0611 | 1429041692.2687 | 1213218546.8278 | 17705245241.9595 | 0.14864 | 180337206.3867 | 105285889.6503 | 88275871.5683
21 |  | 98914932 | 984692.8558 | 1421896483.8074 | 1322981551.8074 | 19028226793.767 | 0.13513 | 178775252.427 | 101602986.825 | 84440716.5855
22 |  | 98914932 | 979769.3915 | 1414787001.3884 | 1315872069.3884 | 20344098863.1553 | 0.12285 | 161649585.4624 | 89430963.9852 | 73672759.8635
23 |  | 98914932 | 974870.5446 | 1407713066.3814 | 1308798134.3814 | 21652896997.5368 | 0.11168 | 146164164.5723 | 78716987.8371 | 64277812.2153
24 |  | 98914932 | 969996.1919 | 1400674501.0495 | 1301759569.0495 | 22954656566.5863 | 0.10153 | 132161918.6932 | 69286422.0889 | 56080818.9113
25 |  | 98914932 | 965146.2109 | 1393671128.5443 | 1294756196.5443 | 24249412763.1305 | 0.092296 | 119500815.556 | 60985545.2566 | 48929042.2404
|  | 12784504510.5773 |  | 37033917273.7079 | 24249412763.1305 |  |  | 12725951826.115 | 10341852634.8141 | 9715614403.7721
[8 empty] | 2834458626.115 | 450359434.8141 | -175878796.2279
[9 empty] | IRR = | 13.72%
[9 empty] | NPV = | 2834458626.115
[9 empty] | PBP = | 6.8145
[9 empty] | PI = | 1.2866
No | item | seri | harga | jumlah | harga total | sumber
1 | Inverter | SG110CX | 78650000 | 10 | 786500000 | https://tokopedia.link/2dXuW31njyb
2 | PV Module | JA SOLAR 540 Wp | 2350000 | 3420 | 8037000000 | https://tokopedia.link/umaeRLJojyb
3 | DC Cable | Cable 6mm2 , 100 m | 3100000 | 36 | 111600000 | https://tokopedia.link/Gb0xmrUojyb
4 | Mounting grounding clip | EZ-GZ-AE | 4000 | 2080 | 8320000 | https://tokopedia.link/vMUDWMBpjyb
5 | Mounting grounding Lug | EZ-GL-U | 15000 | 2080 | 31200000 | https://tokopedia.link/cE6pk9Fpjyb
6 | Mounting End Clamp | ER-EC-AE/35/L50 | 13000 | 2080 | 27040000 | https://tokopedia.link/wCcbJRLpjyb
7 | Mounting Mid Clamp | ER-EC-AE/30-40/L50 478 | 22000 | 4160 | 91520000 | https://tokopedia.link/81HiUS4pjyb
8 | Lighting protecrion | Current cr120 | 2500000 | 3 | 7500000 | https://www.tokopedia.com/indoledlighting/current-cr120-penangkal-petir-lighting-protection-radius-120m-120-m
9 | Grounding cable | 1x6mm Per Meter Super Kabel | 75800 | 3600 | 272880000 | https://www.tokopedia.com/visiotekindo/kabel-nyy-35-mm-kabel-grounding-35mm?extParam=ivf%3Dfalse%26src%3Dsearch
10 | Kabel Tray | Galvanis powder coating Hotdip 2mm | 141191 | 1200 | 169429200 | https://www.tokopedia.com/rajaboxpanel/kabel-cable-tray-tipe-u-elektro-galvanis-powder-coating-hotdip-2mm?extParam=ivf%3Dfalse&src=topads
11 | MC4 connector | Male-Female | 5200 | 3420 | 17784000 | https://www.tokopedia.com/panelsuryaku-8/mc4-socket-connector-solar-panel-surya-solarcell-konektor-ip67
12 | Mounting Rail | Rail 2200mm | 78000 | 3120 | 243360000
13 | Mounting Rail Clamp | ER-RC-AE | 14000 | 6240 | 87360000 | https://tokopedia.link/5LdE1W0qjyb
| total |  | 86968191 |  | 9891493200

## aktual hybrid
Hybrid tidak menjual ke grid | [5 empty] | Asumsi PLTS setiap tahunnya energi yang dihasilkan PLTS menurun 0,5%
Tahun | Investasi Awal (Rp) | Arus Kas Keluar (Rp) pertahun | Penghematan atau Energi yang di import(kWh) | Arus Kas Masuk (Rp) | Arus Kas Bersih(Rp) | kumulative arus kas bersih(Rp) | Faktor Diskonto | Present Value (Rp) | IRR | IRR
- | 12884194420 | 12884194420 |  |  | -12884194420 | -12884194420 | 1 | -12884194420 | 11% | 12%
1 |  | 128841944.2 | 1226878.24 | 1771612178.56 | 1642770234.36 | -11241424185.64 | 0.90909 | 1493427485.7818 | 1479973184.1081 | 1466759137.8214
2 |  | 128841944.2 | 1214640.1296 | 1753940347.0789 | 1625098402.8789 | -9616325782.7611 | 0.82645 | 1343056531.3048 | 1318966320.0056 | 1295518497.193
3 |  | 128841944.2 | 1208566.9289 | 1745170645.3435 | 1616328701.1435 | -7999997081.6177 | 0.75131 | 1214371676.2911 | 1181845615.6255 | 1150470843.4478
4 |  | 128841944.2 | 1202524.0943 | 1736444792.1168 | 1607602847.9168 | -6392394233.7009 | 0.68301 | 1098014376.0103 | 1058977790.0465 | 1021660672.7462
5 |  | 128841944.2 | 1196511.4738 | 1727762568.1562 | 1598920623.9562 | -4793473609.7447 | 0.62092 | 992803909.2934 | 948881567.747 | 907270502.1951
6 |  | 128841944.2 | 1190528.9164 | 1719123755.3154 | 1590281811.1154 | -3203191798.6294 | 0.56447 | 897672623.8133 | 850229597.1115 | 805686256.9533
7 |  | 128841944.2 | 1184576.2718 | 1710528136.5388 | 1581686192.3388 | -1621505606.2905 | 0.51316 | 811655110.0921 | 761832457.9298 | 715474508.0137
8 |  | 128841944.2 | 1178653.3905 | 1701975495.8561 | 1573133551.6561 | -48372054.6344 | 0.46651 | 733878411.9031 | 682624330.279 | 635362256.8855
9 |  | 128841944.2 | 1172760.1235 | 1693465618.3768 | 1564623674.1768 | 1516251619.5424 | 0.4241 | 663553173.8676 | 611650152.2167 | 564218982.2317
10 |  | 462706347.9799 | 1166896.3229 | 1684998290.285 | 1222291942.305 | 2738543561.8474 | 0.38554 | 471246456.0795 | 430472250.6109 | 393545292.7227
11 |  | 128841944.2 | 1161061.8413 | 1676573298.8335 | 1547731354.6335 | 4286274916.4809 | 0.35049 | 542470397.8351 | 491069333.7068 | 444935780.0217
12 |  | 128841944.2 | 1155256.5321 | 1668190432.3394 | 1539348488.1394 | 5825623404.6203 | 0.31863 | 490483867.517 | 440008639.6783 | 395112416.2685
13 |  | 128841944.2 | 1149480.2494 | 1659849480.1777 | 1531007535.9777 | 7356630940.598 | 0.28966 | 443478348.2812 | 394256265.8042 | 350867412.1403
14 |  | 128841944.2 | 1143732.8482 | 1651550232.7768 | 1522708288.5768 | 8879339229.1747 | 0.26333 | 400976683.5732 | 353260442.6022 | 311576284.6773
15 |  | 128841944.2 | 1138014.1839 | 1643292481.6129 | 1514450537.4129 | 10393789766.5876 | 0.23939 | 362547417.8195 | 316526745.1062 | 276684451.0549
16 |  | 709389426.8338 | 1132324.113 | 1635076019.2048 | 925686592.371 | 11319476358.9587 | 0.21763 | 201456373.1102 | 174299568.8662 | 150999535.2934
17 |  | 128841944.2 | 1126662.4925 | 1626900639.1088 | 1498058694.9088 | 12817535053.8675 | 0.19784 | 296382926.4872 | 254119615.9185 | 218183771.2964
18 |  | 128841944.2 | 1121029.18 | 1618766135.9133 | 1489924191.7133 | 14307459245.5807 | 0.17986 | 267975962.178 | 227693458.4311 | 193749131.1961
19 |  | 128841944.2 | 1115424.0341 | 1610672305.2337 | 1481830361.0337 | 15789289606.6144 | 0.16351 | 242291105.0784 | 204014902.3486 | 172050547.1179
20 |  | 257561124.6567 | 1109846.9139 | 1602618943.7075 | 1345057819.0508 | 17134347425.6652 | 0.14864 | 199934274.1259 | 166832776.5583 | 139437792.9475
21 |  | 128841944.2 | 1104297.6794 | 1594605848.989 | 1465763904.789 | 18600111330.4542 | 0.13513 | 198069513.3042 | 163787769.3531 | 135670537.8406
22 |  | 128841944.2 | 1098776.191 | 1586632819.744 | 1457790875.544 | 20057902205.9982 | 0.12285 | 179083739.373 | 146753914.4658 | 120475497.6338
23 |  | 128841944.2 | 1093282.31 | 1578699655.6453 | 1449857711.4453 | 21507759917.4435 | 0.11168 | 161917438.278 | 131491255.0788 | 106982036.6402
24 |  | 128841944.2 | 1087815.8985 | 1570806157.3671 | 1441964213.1671 | 22949724130.6106 | 0.10153 | 146396279.0288 | 117815652.0702 | 94999635.3023
25 |  | 128841944.2 | 1082376.819 | 1562952126.5803 | 1434110182.3803 | 24383834312.9909 | 0.092296 | 132362630.7787 | 105562106.9097 | 84359102.8879
|  | 17148374091.8705 | 28761917.1779 | 41532208404.8614 | 24383834312.9909 |  |  | 13985506711.2058 | 13012945712.5785 | 12152050882.529
[10 empty] | 128751292.5785 | -732143537.471
No | item | seri | harga | jumlah | harga total | sumber |  |  | IRR= | 11.15%
1 | PV Module | JA SOLAR 540 Wp | 2350000 | 3420 | 8037000000 | https://tokopedia.link/umaeRLJojyb |  |  | NPV= | 1101312291.2058
2 | Baterai | EVE LF100MA 48 V 100ah Lifepo4 | 7800000 | 342 | 2667600000 | https://www.tokopedia.com/baterailab/baterai-lithium-lifepo4-3-2v-100ah-discharge-capacity-test-prove-eve-100ah-c7528 |  |  | PBP | 8.0309
3 | DC Cable | Cable 6mm2 , 100 m | 3100000 | 36 | 111600000 | https://www.tokopedia.com/badank/100m-black-red-6mm2-solar-pv-cable-h1z2z2-k-1500v-tinned-copper?extParam=ivf%3Dfalse%26src%3Dsearch&refined=true |  |  | PI | 1.0855
4 | Mounting grounding clip | EZ-GZ-AE | 4000 | 2080 | 8320000 | https://tokopedia.link/vMUDWMBpjyb
5 | Mounting grounding Lug | EZ-GL-U | 15000 | 2080 | 31200000 | https://tokopedia.link/cE6pk9Fpjyb
6 | Mounting End Clamp | ER-EC-AE/35/L50 | 13000 | 2080 | 27040000 | https://tokopedia.link/wCcbJRLpjyb
7 | Mounting Mid Clamp | ER-EC-AE/30-40/L50 478 | 22000 | 4160 | 91520000 | https://tokopedia.link/81HiUS4pjyb
8 | Hybrid Inverter | ATESS HPS 100 | 86595828 | 10 | 865958280 | https://indonesian.alibaba.com/p-detail/ATESS-1600700727460.html?spm=a2700.galleryofferlist.p_offer.d_title.375435e4XxCGbF&s=p
9 | beacukai |  | 238642940 |  | 238642940
10 | Lighting protecrion | Current cr120 | 2500000 | 3 | 7500000 | https://www.tokopedia.com/indoledlighting/current-cr120-penangkal-petir-lighting-protection-radius-120m-120-m
11 | Grounding cable | 1x6mm Per Meter Super Kabel | 75800 | 3600 | 272880000 | https://www.tokopedia.com/visiotekindo/kabel-nyy-35-mm-kabel-grounding-35mm?extParam=ivf%3Dfalse%26src%3Dsearch
12 | MC4 connector | Male-Female | 5200 | 3420 | 17784000 | https://www.tokopedia.com/panelsuryaku-8/mc4-socket-connector-solar-panel-surya-solarcell-konektor-ip67
13 | Kabel Tray | Galvanis powder coating Hotdip 2mm | 141191 | 1200 | 169429200 | https://www.tokopedia.com/rajaboxpanel/kabel-cable-tray-tipe-u-elektro-galvanis-powder-coating-hotdip-2mm?extParam=ivf%3Dfalse&src=topads
14 | Mounting Rail | Rail 2200mm | 78000 | 3120 | 243360000
15 | Mounting Rail Clamp | ER-RC-AE | 14000 | 6240 | 87360000 | https://tokopedia.link/5LdE1W0qjyb
16 | kWh Exim | Edmi Mk6N | 7000000 | 1 | 7000000 | http://en.integra-solusi.co.id/product/kwh-meter-edmi-mk6n-class-05s-p969115.aspx
| Total |  | 348356959 |  | 12884194420

## LCOE
Tahun | Energi pertahun(kWh) | Et(kWh) | PV Et | LCC hybrid (Rp) | LCC on-grid (Rp) | PV LCC Hybrid | PV LCC On-grid
0 |  |  |  | 12884194420 | 9891493200 | 12884194420 | 9891493200
1 | 1238207 | 1232015.965 | 1140755.5231 | 128841944.2 | 98914932 | 117129040.1818 | 89922665.4545
2 | 1238207 | 1225855.8852 | 1050973.8385 | 128841944.2 | 98914932 | 106480945.6198 | 81747877.686
3 | 1238207 | 1219726.6057 | 968258.3049 | 128841944.2 | 98914932 | 96800859.6544 | 74316252.4418
4 | 1238207 | 1213627.9727 | 892052.7901 | 128841944.2 | 98914932 | 88000781.504 | 67560229.4925
5 | 1238207 | 1207559.8329 | 821844.9317 | 128841944.2 | 98914932 | 80000710.4582 | 61418390.4477
6 | 1238207 | 1201522.0337 | 757162.6917 | 128841944.2 | 98914932 | 72727918.5983 | 55834900.407
7 | 1238207 | 1195514.4235 | 697571.1835 | 128841944.2 | 98914932 | 66116289.6349 | 50759000.37
8 | 1238207 | 1189536.8514 | 642669.7478 | 128841944.2 | 98914932 | 60105717.8499 | 46144545.7909
9 | 1238207 | 1183589.1671 | 592089.2584 | 128841944.2 | 98914932 | 54641561.6817 | 41949587.0827
10 | 1238207 | 1177671.2213 | 545489.6408 | 462706347.9799 | 402144729.1363 | 178393327.4401 | 155044201.698
11 | 1238207 | 1171782.8652 | 502557.5858 | 128841944.2 | 98914932 | 45158315.4394 | 34669080.2336
12 | 1238207 | 1165923.9509 | 463004.4424 | 128841944.2 | 98914932 | 41053014.0358 | 31517345.6669
13 | 1238207 | 1160094.3311 | 426564.278 | 128841944.2 | 98914932 | 37320921.8508 | 28652132.4245
14 | 1238207 | 1154293.8595 | 392992.0894 | 128841944.2 | 98914932 | 33928110.7734 | 26047393.1132
15 | 1238207 | 1148522.3902 | 362062.1565 | 128841944.2 | 98914932 | 30843737.0667 | 23679448.2847
16 | 1238207 | 1142779.7782 | 333566.5238 | 709389426.8338 | 98914932 | 154383807.9005 | 21526771.1679
17 | 1238207 | 1137065.8793 | 307313.6029 | 128841944.2 | 98914932 | 25490691.7907 | 19569791.9708
18 | 1238207 | 1131380.5499 | 283126.8842 | 128841944.2 | 98914932 | 23173356.1734 | 17790719.9735
19 | 1238207 | 1125723.6472 | 260843.7498 | 128841944.2 | 98914932 | 21066687.4303 | 16173381.7941
20 | 1238207 | 1120095.0289 | 240314.3806 | 257561124.6567 | 215823145.441 | 38284820.007 | 32080735.3499
21 | 1238207 | 1114494.5538 | 221400.7488 | 128841944.2 | 98914932 | 17410485.4796 | 13366431.2348
22 | 1238207 | 1108922.081 | 203975.6898 | 128841944.2 | 98914932 | 15827714.0724 | 12151301.1225
23 | 1238207 | 1103377.4706 | 187922.0476 | 128841944.2 | 98914932 | 14388830.9749 | 11046637.3841
24 | 1238207 | 1097860.5833 | 173131.8864 | 128841944.2 | 98914932 | 13080755.4317 | 10042397.6219
25 | 1238207 | 1092371.2804 | 159505.7657 | 128841944.2 | 98914932 | 11891595.847 | 9129452.3836
Total | 30955175 | 29021308.2082 | 12627149.7422 | 17148374091.8705 | 12784504510.5773 | 14327894416.8967 | 10923633870.5971
LCOE Hybrid | 1134.6895
LCOE On-grid | 865.091